## pg1
By Zakaria Al-Mutawakel
Line | Area seved |  | future pop | Wat. Cons | Domestic ww |  |  | Indust | Design | Length | min dia | min slope | G.L (m) |  | ground slope | used slope | I.L (m) |  | Full flow |  | Partial flow |  |  |  | Remarks | Comments
[19 empty] | Vfull | Qfull | q/Q | h/D | v/V | Velocity
| Partial | cum | no | m3/d | Qav(l/s) | Qmax(l/s) | Qmin(l/s) | Qind(l/s) | Qdes(l/s) | m | mm | %o | up | down | %o | %o | up | down | m/s | l/s | l/s |  |  | m/s
1--2 | 0.0633 | 0.0633 | 133 | 22 | 0.2 | 0.4 | 0.1 | 1.157 | 1.6 | 24.5 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.69 | 0.61 | 10.78 | 0.15 | 0.265 |  | 0 | v<vmin | ok
5--2 | 0.4189 | 0.4189 | 878 | 145 | 1.3 | 2.5 | 0.4 | 0 | 2.5 | 72.6 | 150 | 6.67 | 102 | 98 | 55.1 | 55.1 | 100.85 | 96.85 | 1.75 | 30.93 | 0.08 | 0.187 |  |  |  | ok
2-2a | 0.0498 | 0.532 | 1114 | 184 | 1.7 | 3.3 | 0.5 | 1.157 | 4.5 | 23.6 | 150 | 6.67 | 98 | 100 | -84.75 | 6.67 | 96.85 | 96.69 | 0.61 | 10.78 | 0.42 | 0.467 |  |  |  | ok
2a-3 | 0.0469 | 0.5789 | 1213 | 200 | 1.9 | 3.7 | 0.6 | 1.157 | 4.9 | 23.6 | 150 | 6.67 | 100 | 100 | 0 | 6.67 | 98.85 | 98.69 | 0.61 | 10.78 | 0.45 | 0.485 |  |  |  | ok
4--3 | 0.1854 | 0.1854 | 389 | 64 | 0.6 | 1.2 | 0.2 | 0 | 1.2 | 26.4 | 150 | 6.67 | 98 | 100 | -75.76 | 6.67 | 96.85 | 96.67 | 0.61 | 10.78 | 0.11 | 0.223 |  |  |  | ok
3--9 | 0.2086 | 0.9729 | 2038 | 336 | 3.1 | 6 | 0.9 | 1.157 | 7.2 | 62.3 | 150 | 6.67 | 100 | 98 | 32.1 | 32.1 | 98.85 | 96.85 | 1.34 | 23.68 | 0.3 | 0.388 |  |  |  | ok
6--8 | 0.0231 | 0.0231 | 49 | 8 | 0.1 | 0.2 | 0 | 0 | 0.2 | 30.2 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.65 | 0.61 | 10.78 | 0.02 | 0.087 |  |  |  | ok
7--8 | 0.147 | 0.147 | 308 | 51 | 0.5 | 1 | 0.2 | 0 | 1 | 31.2 | 150 | 6.67 | 102 | 98 | 128.21 | 128.21 | 100.85 | 96.85 | 2.67 | 47.18 | 0.02 | 0.087 |  |  |  | ok
8--9 | 0.0355 | 0.2056 | 431 | 71 | 0.7 | 1.4 | 0.2 | 0 | 1.4 | 31.2 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.64 | 0.61 | 10.78 | 0.13 | 0.244 |  |  |  | ok
9--9a | 0.0567 | 1.2352 | 2587 | 427 | 4 | 7.8 | 1.2 | 1.157 | 9 | 26.4 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.67 | 0.61 | 10.78 | 0.83 | 0.681 |  |  |  | ok
9a--9b | 0.0543 | 1.2895 | 2700 | 446 | 4.1 | 8 | 1.2 | 1.157 | 9.2 | 25.5 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.68 | 0.61 | 10.78 | 0.85 | 0.69 |  |  |  | ok
9b--11 | 0.0643 | 1.3538 | 2835 | 468 | 4.3 | 8.4 | 1.3 | 1.157 | 9.6 | 23.6 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.69 | 0.61 | 10.78 | 0.89 | 0.707 |  |  |  | ok
10--11 | 0.0809 | 0.0809 | 170 | 28 | 0.3 | 0.6 | 0.1 | 0 | 0.6 | 34 | 150 | 6.67 | 102 | 98 | 117.65 | 117.65 | 100.85 | 96.85 | 2.56 | 45.24 | 0.01 | 0.059 |  |  |  | ok
11--12 | 0.0113 | 1.446 | 3028 | 500 | 4.6 | 9 | 1.4 | 1.157 | 10.2 | 13.2 | 200 | 5 | 98 | 98 | 0 | 5 | 96.85 | 96.78 | 0.64 | 20.11 | 0.51 | 0.52 |  |  |  | ok
12--19 | 0.067 | 1.513 | 3168 | 523 | 4.8 | 9.4 | 1.4 | 1.157 | 10.6 | 98 | 200 | 5 | 98 | 98 | 0 | 5 | 96.85 | 96.36 | 0.64 | 20.11 | 0.53 | 0.531 |  |  |  | ok
5--5a | 0.2819 | 0.2819 | 591 | 98 | 0.9 | 1.8 | 0.3 | 0 | 1.8 | 50 | 150 | 6.67 | 102 | 98 | 80 | 80 | 100.85 | 96.85 | 2.11 | 37.29 | 0.05 | 0.144 |  |  |  | ok
5a-14 | 0.1384 | 0.4203 | 881 | 145 | 1.3 | 2.5 | 0.4 | 0 | 2.5 | 37 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.6 | 0.61 | 10.78 | 0.23 | 0.335 |  |  |  | ok
13-13a | 0.1154 | 0.1154 | 242 | 40 | 0.4 | 0.8 | 0.1 | 0 | 0.8 | 25.5 | 150 | 6.67 | 102 | 100 | 78.43 | 78.43 | 100.85 | 98.85 | 2.09 | 36.93 | 0.02 | 0.087 |  |  |  | ok
13a-14 | 0.1656 | 0.281 | 589 | 97 | 0.9 | 1.8 | 0.3 | 0 | 1.8 | 49 | 150 | 6.67 | 100 | 98 | 40.82 | 40.82 | 98.85 | 96.85 | 1.51 | 26.68 | 0.07 | 0.174 |  |  |  | ok
14--16 | 0.0404 | 0.7417 | 1553 | 256 | 2.4 | 4.7 | 0.7 | 0 | 4.7 | 30.2 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.65 | 0.61 | 10.78 | 0.44 | 0.479 |  |  |  | ok
15--16 | 0.0749 | 0.0749 | 157 | 26 | 0.2 | 0.4 | 0.1 | 0 | 0.4 | 38.5 | 150 | 6.67 | 104 | 98 | 155.84 | 155.84 | 102.85 | 96.85 | 2.95 | 52.13 | 0.01 | 0.059 |  |  |  | ok
7--16 | 0.2306 | 0.2306 | 483 | 80 | 0.7 | 1.4 | 0.2 | 0 | 1.4 | 72.5 | 150 | 6.67 | 102 | 98 | 55.17 | 55.17 | 100.85 | 96.85 | 1.75 | 30.93 | 0.05 | 0.144 |  |  |  | ok
16--18 | 0.0422 | 1.0894 | 2281 | 376 | 3.5 | 6.8 | 1.1 | 0 | 6.8 | 35.5 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.61 | 0.61 | 10.78 | 0.63 | 0.584 |  |  |  | ok
17--18 | 0.0437 | 0.0437 | 92 | 15 | 0.1 | 0.2 | 0 | 0 | 0.2 | 27.5 | 150 | 6.67 | 102 | 98 | 145.45 | 145.45 | 100.85 | 96.85 | 2.85 | 50.36 | 0 | 0 |  |  |  | ok
10--10a | 0.1205 | 0.1205 | 253 | 42 | 0.4 | 0.8 | 0.1 | 0 | 0.8 | 23.5 | 150 | 6.67 | 102 | 98 | 170.21 | 170.21 | 100.85 | 96.85 | 3.08 | 54.43 | 0.01 | 0.059 |  |  |  | ok
10a--18 | 0.0386 | 0.1591 | 334 | 55 | 0.5 | 1 | 0.2 | 0 | 1 | 25.5 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.68 | 0.61 | 10.78 | 0.09 | 0.2 |  |  |  | ok
18--19 | 0.0446 | 1.3368 | 2799 | 462 | 4.3 | 8.4 | 1.3 | 0 | 8.4 | 17 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.74 | 0.61 | 10.78 | 0.78 | 0.658 |  |  |  | ok
19--19a | 0.1088 | 2.9586 | 6195 | 1022 | 9.5 | 18.5 | 2.9 | 1.157 | 19.7 | 85 | 250 | 4 | 98 | 98 | 0 | 4 | 96.85 | 96.51 | 0.66 | 32.4 | 0.61 | 0.574 |  |  |  | ok
19a--22 | 0.0518 | 3.0104 | 6304 | 1040 | 9.6 | 18.7 | 2.9 | 1.157 | 19.9 | 85 | 250 | 4 | 98 | 98 | 0 | 4 | 96.85 | 96.51 | 0.66 | 32.4 | 0.61 | 0.574 |  |  |  | ok
13-20 | 0.1704 | 0.1704 | 357 | 59 | 0.5 | 1 | 0.2 | 0 | 1 | 28.3 | 150 | 6.67 | 102 | 98 | 141.34 | 141.34 | 100.85 | 96.85 | 2.81 | 49.66 | 0.02 | 0.087 |  |  |  | ok
15--20 | 0.0992 | 0.0992 | 208 | 34 | 0.3 | 0.6 | 0.1 | 0 | 0.6 | 51.8 | 150 | 6.67 | 104 | 98 | 115.83 | 115.83 | 102.85 | 96.85 | 2.54 | 44.89 | 0.01 | 0.059 |  |  |  | ok
20-21 | 0.0822 | 0.3518 | 737 | 122 | 1.1 | 2.1 | 0.3 | 0 | 2.1 | 32.14 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.64 | 0.61 | 10.78 | 0.19 | 0.301 |  |  |  | ok
17--21 | 0.1449 | 0.1449 | 304 | 50 | 0.5 | 1 | 0.2 | 0 | 1 | 54 | 150 | 6.67 | 102 | 98 | 74.07 | 74.07 | 100.85 | 96.85 | 2.03 | 35.87 | 0.03 | 0.109 |  |  |  | ok
21-21a | 0.2245 | 0.7212 | 1511 | 249 | 2.3 | 4.5 | 0.7 | 0 | 4.5 | 61.32 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.44 | 0.61 | 10.78 | 0.42 | 0.467 |  |  |  | ok
21a-22 | 0.0373 | 0.7585 | 1589 | 262 | 2.4 | 4.7 | 0.7 | 0 | 4.7 | 18.9 | 150 | 6.67 | 98 | 98 | 0 | 6.67 | 96.85 | 96.72 | 0.61 | 10.78 | 0.44 | 0.479 |  |  |  | ok
END | 0 | 3.7689 | 7892 | 1302 | 12.1 | 23.6 | 3.6 | 1.157 | 24.8 |  | 250 | 4 | 98 | 98 |  | 4 | 96.85 | 96.85 | 0.66 | 32.4 | 0.77 |  |  |  |  | ok
.

## pg2
Dmin | min slop %0 | velocity Vf(m/s) | flow Qf (l/s)
150 | 6.67 | 0.61 | 11
200 | 5 | 0.64 | 20
250 | 4 | 0.66 | 32
300 | 3.33 | 0.68 | 48
400 | 2.5 | 0.72 | 90
500 | 2 | 0.75 | 147
600 | 1.67 | 0.77 | 218
700 | 1.43 | 0.79 | 304
800 | 1.25 | 0.81 | 407
900 | 1.11 | 0.82 | 522
1000 | 1 | 0.84 | 660
1100 | 0.91 | 0.85 | 808
1200 | 0.83 | 0.86 | 973
1300 | 0.77 | 0.87 | 1155

## pg3
q | h | V | R | q | h | V | R | <7 | h | V | R
Qfull | D | Vfull | D | Qfull | D | Vfull | D | Qfull | D | Vfull | D
0.001 | 0.023 | 0.17 | 0.0152 | 0.21 | 0.309 | 0.8 | 0.1751 | 0.805 | 0.701 | 1.08 | 0.2964
2 | 0.032 | 0.21 | 0.021 | 0.22 | 0.316 | 0.81 | 0.1784 | 0.81 | 0.705 | 0.08 | 0.2969
3 | 0.038 | 0.24 | 0.0249 | 0.23 | 0.324 | 0.82 | 0.182 | 0.815 | 0.709 | 0.08 | 0.2974
4 | 0.044 | 0.26 | 0.0287 | 0.24 | 0.331 | 0.83 | 0.1851 | 0.82 | 0.713 | 0.08 | 0.2979
5 | 0.049 | 0.28 | 0.0319 | 0.25 | 0.339 | 0.84 | 0.1887 | 0.825 | 0.717 | 0.08 | 0.2984
6 | 0.053 | 0.29 | 0.0345 | 0.26 | 0.346 | 0.85 | 0.1918 | 0.83 | 0.721 | 0.08 | 0.2989
7 | 0.057 | 0.3 | 0.037 | 0.27 | 0.353 | 0.86 | 0.1948 | 0.835 | 0.725 | 0.08 | 0.2993
8 | 0.061 | 0.32 | 0.0395 | 0.28 | 0.36 | 0.86 | 0.1978 | 0.84 | 0.729 | 0.07 | 0.2997
9 | 0.065 | 0.33 | 0.042 | 0.29 | 0.367 | 0.87 | 0.2007 | 0.845 | 0.734 | 0.07 | 0.3002
0.01 | 0.068 | 0.34 | 0.0439 | 0.3 | 0.374 | 0.88 | 0.2037 | 0.855 | 0.738 | 1.07 | 0.3006
11 | 0.071 | 0.35 | 0.0458 | 0.31 | 0.381 | 0.89 | 0.2066 | 0.855 | 0.742 | 0.07 | 0.301
12 | 0.074 | 0.36 | 0.0476 | 0.32 | 0.387 | 0.89 | 0.209 | 0.86 | ,747 j | 0.07 | 0.3014
13 | 0.077 | 0.36 | 0.0495 | 0.33 | 0.394 | 0.9 | 0.2118 | 0.865 | ,751 ' | 0.07 | 0.3018
L4 | 0.08 | 0.37 | 0.0513 | 0.34 | 0.401 | 0.91 | 0.2146 | 0.87 | 0.756 | 0.07 | 0.3022
15 | 0.083 | 0.38 | 0.0532 | 0.35 | 0.407 | 0.92 | 0.217 | 0.875 | 0.761 | 0.07 | 0.3025
16 | 0.086 | 0.39 | 0.055 | 0.36 | 0.414 | 0.92 | 0.2197 | 0.88 | 0.766 | 0.07 | 0.3028
17 | 0.088 | 0.39 | 0.0562 | 0.37 | 0.42 | 0.93 | 0.222 | 0.885 | 0.77 | 0.07 | 0.3031
18 | 0.091 | 0.4 | 0.0581 | 0.38 | 0.426 | 0.93 | 0.2243 | 0.89 | 0.775 | 0.07 | 0.3033
19 | 0.093 | 0.41 | 0.0593 | 0.39 | 0.433 | 0.94 | 0.2269 | 0.895 | 0.781 | 0.07 | 0.3036
0.02 | 0.095 | 0.41 | 0.0605 | 0,400) | 0.439 | CO,95. | 0.2291 | 0.9 | 0.786 | 1.07 | 0.3038
22 | 0.1 | 0.42 | 0.0635 | 0.41 | 0.445 | 0.95 | 0.2313 | 0.905 | 0.791 | 0.07 | 0.304
24 | 0.104 | 0.43 | 0.0659 | 0.42 | 0.451 | 0.96 | 0.2334 | 0.91 | 0.797 | 0.07 | 0.3041
26 | 0.108 | 0.45 | 0.0683 | 0.43 | 0.458 | 0.96 | 0.2359 | 0.915 | 0.803 | 0.06 | 0.3042
28 | 0.112 | 0.45 | 0.0707 | 0.44 | 0.464 | 0.97 | 0.238 | 0.92 | ,808- | 0.06 | 0.3043
30 | 0.116 | 0.46 | 0.0731 | 0.45 | 0.47 | 0.97 | 0.2401 | 0.925 | 0.814 | 0.06 | 0.3043
32 | 0.12 | 0.47 | 0.0755 | 0.46 | 0.476 | 0.98 | 0.242 | 0.93 | 0.821 | 0.06 | 0.3043
34 | 0.123 | 0.48 | 0.0772 | 0.47 | 0.482 | 0.99 | 0.2441 | 0.935 | 0.827 | 0.06 | 0.3042
36 | 0.127 | 0.49 | 0.0796 | 0.48 | 0.488 | 0.99 | 0.2461 | 0.94 | 0.834 | 0.05 | 0.304
. 38 | 0.13 | 0.5 | 0.0813 | 0.49 | 0.494 | 1 | 0.2481 | 0.945 | 0.841 | 0.05 | 0.3037
0.04 | 0.134 | 0.,50 | 0.0837 | 0.5 | i 0,500 | 1,00. | 0.25 | 0.95 | 0.849 | 1.05 | 0.3033
45 | 0.141 | 0.52 | 0.0877 | 0.51 | 0.506 | 0 | 0.2519 | 0.955 | 0.856 | 0.05 | 0.3029
50 | 0.149 | 0.54 | 0.0923 | 0.52 | 0.512 | 0.01 | 0.2538 | 0.96 | 0.865 | 0.04 | 0.3022
55 | 0.156 | 0.55 | 0.0963 | 0.53 | 0.519 | 0.01 | 0.2559 | 0.965 | 0.874 | 0.04 | 0.3014
60 | 0.163 | 0.57 | 0.1002 | 0.54 | 0.525 | 0.02 | 0.2577 | 0.97 | 0.883 | 0.04 | 0.3004
65 | 0.17 | 0.58 | 0.1042 | 0.55 | 0.531 | 0.02 | 0.2595 | 0.975 | 0.894 | 0.03 | 0.2989
70 | 0.176 | 0.59 | 0.1075 | 0.56 | 0.537 | 0.02 | 0.2612 | 0.98 | 0.905 | 0.03 | 0.2972
75 | 0.182 | 0.6 | 0.1108 | 0.57 | 0.543 | 0.03 | 0.2629 | 0.985 | 0.919 | 0.02 | 0.2946
80 | 0.188 | 0.61 | 0.1141 | 0.58 | 0.55 | 0.03 | 0.2649 | 0.99 | 0.935 | 0.02 | 0.2908
85 | 0.194 | 0.62 | 0.1174 | 0.59 | 0.556 | 0.03 | 0.2665 | 0.995 | 0.956 | 0.01 | 0.2844
0.09 | 0.2 | 0.63 | 0.1206 | 0.6 | 0.562 | 1.04 | 0.2681 | 1 | 1 | 1 | 0.25
0.095 | 0.205 | 0.64 | 0.1233 | 0.61 | 0.568 | 0.04 | 0.2697
100 | 0.211 | 0.65 | 0.1265 | 0.62 | 0.575 | 0.04 | 0.2715
0.105 | 0.216 | 0.66 | 0.1291 | 0.63 | 0.581 | 0.05 | 0.2731
0.11 | 0.221 | 0.67 | 0.1317 | 0.64 | 0.587 | 0.05 | 0.2745
0.115 | 0.226 | 0.68 | 0.1343 | 0.65 | 0.594 | 0.05 | 0.2762
0.12 | 0.231 | 0.69 | 0.1369 | 0.66 | 0.6 | 0.05 | 0.2776
0.125 | 0.236 | 0.69 | 0.1395 | 0.67 | :607 | 0.06 | 0.2793
0.13 | 0.241 | ,70. | 0.1421 | 0.68 | 0.613 | 0.06 | 0.2806
0.135 | 0.245 | 0.71 | 0.1441 | 0.69 | 0.62 | 0.06 | 0.2821
0.14 | 0.25 | 0.72 | 0.1466 | 0.7 | 0.626 | 1.06 | 0.2834
0.145 | 0.255 | 0.72 | 0.4491 | 0.71 | 0.633 | 0.06 | 0.2848
0.15 | 0.259 | 0.73 | 0.1511 | 0.72 | 0.64 | 0.07 | 0.2862
0.155 | 0.263 | 0.74 | 0.1531 | 0.73 | 0.646 | 0.07 | 0.2874
0.16 | 0.268 | 0.74 | 0.1556 | 0.74 | 0.653 | 0.07 | 0.2887
0.165 | 0.272 | 0.75 | 0.1575 | 0.75 | 0.66 | 0.07 | 0.29
0.17 | 0.276 | 0.76 | 0.1595 | 0.76 | 0.667 | 0.07 | 0.2912
0.175 | 0.281 | 0.76 | 0.1619 | 0.77 | 0.675 | 0.07 | 0.2925
- ,180 | 0.285 | 0.77 | 0.1638 | 0.78 | 0.682 | 0.07 | 0.2936
0.19 | 0.293 | 0.78 | 0.1676 | 0.79 | 0.689 | 0.07 | 0.2947
0,200. | 0.301 | 0.79 | 0.1714 | 0.8 | 0.697 | 1.07 | 80.295